## Compliance Week of 20 Jul – 26
Substation | Meter | Role | Voltage | THD | Unbalance | Frequency | Availability % | Overall
Driefontein Substation's | Busbar (Eskom supply) | BUSBAR | 101.55–103.98% | 1.8% | FAIL ok | ok | 58 | FAIL FAIL
Driefontein Substation's | Ballito Sub (Feeder 1) (33KV) | Feeder | 100.76–105.12% | 1.2% | FAIL ok | ok | 58 | FAIL FAIL
Driefontein Substation's | Zimbali Sub (Feeder 2) (33KV) | Feeder | 100.59–104.55% | 2.5% | FAIL ok | ok | 58 | FAIL FAIL
Shakaskraal Substation | Busbar (Eskom supply) | BUSBAR | 102.05–104.94% | 1.05% | FAIL ok | ok | 58 | FAIL FAIL
Shakaskraal Substation | Shakaskraal-Feeder 1 (North) (33KV) | Feeder | 101.7–104.68% | 0.8% | FAIL ok | ok | 58 | FAIL FAIL
Shakaskraal Substation | Shakaskraal-Feeder 2 (South) (33KV) | Feeder | 102.3–105.34% | 1.4% | FAIL ok | ok | 58 | FAIL FAIL
Stanger Substation | Busbar (Eskom supply) | BUSBAR | 102.08–105.47% | 0.92% | 1.06% | ok | 100 | PASS
Stanger Substation | Stanger-Feeder 1 (33KV) | Feeder | 102.1–105.37% | 0.9% | 1.07% | ok | 58 | PASS
Stanger Substation | Stanger-Feeder 2 (33kV) | Feeder | 102.07–105.47% | 0.9% | 1.09% | ok | 58 | PASS
Stanger Substation | Stanger-Gelnhills Feed (33KV) | Feeder | 102.08–105.35% | 0.9% | 1.07% | ok | 58 | PASS
Stanger Substation | Stanger-Groutville Phase1 (33KV) | Feeder | 99.34–108.62% | 1.7% | FAIL 4.14% | ok | 58 | FAIL FAIL
Stanger Substation | Stanger-Sappi Feed 1 (33KV) | Feeder | 102.07–105.45% | 0.9% | 1.06% | ok | 100 | PASS
Stanger Substation | Stanger-Sappi Feed 2 (33KV) | Feeder | 102.07–105.35% | 0.9% | 1.08% | ok | 57 | PASS

## Findings
Substation | Responsibility | Parameter | Where | Detail
Driefontein Substation's | ESKOM | unbalance | busbar (all feeders) | Busbar voltage unbalance breaches at the busbar — shared supply issue → Eskom point of supply
Shakaskraal Substation | ESKOM | unbalance | busbar (all feeders) | Busbar voltage unbalance breaches at the busbar — shared supply issue → Eskom point of supply
Stanger Substation | MUNICIPALITY | unbalance | 10266107 | Busbar voltage unbalance OK at busbar but failing on feeder(s) 10266107 → local network issue