## Compliance Week of 21 Sep – 27
Substation | Meter | Role | Voltage | THD | Unbalance | Frequency | Availability % | Overall
Driefontein Substation's | Busbar (Eskom supply) | BUSBAR | 100.61–103.49% | 1.5% | FAIL ok | ok | 5 | FAIL FAIL
Driefontein Substation's | Ballito Sub (Feeder 1) (33KV) | Feeder | 100.99–104.27% | 1.0% | FAIL ok | ok | 5 | FAIL FAIL
Driefontein Substation's | Zimbali Sub (Feeder 2) (33KV) | Feeder | 100.47–104.41% | 2.1% | FAIL ok | ok | 5 | FAIL FAIL
Shakaskraal Substation | Busbar (Eskom supply) | BUSBAR | 101.99–103.69% | 0.9% | FAIL ok | ok | 5 | FAIL FAIL
Shakaskraal Substation | Shakaskraal-Feeder 1 (North) (33KV) | Feeder | 101.6–103.43% | 0.7% | FAIL ok | ok | 5 | FAIL FAIL
Shakaskraal Substation | Shakaskraal-Feeder 2 (South) (33KV) | Feeder | 102.21–103.81% | 1.2% | FAIL ok | ok | 5 | FAIL FAIL
Stanger Substation | Busbar (Eskom supply) | BUSBAR | 101.81–105.2% | 0.93% | 1.0% | ok | 57 | PASS
Stanger Substation | Stanger-Feeder 1 (33KV) | Feeder | 101.8–105.05% | 0.9% | 1.0% | ok | 5 | PASS
Stanger Substation | Stanger-Feeder 2 (33kV) | Feeder | 101.78–105.19% | 0.84% | 1.0% | ok | 5 | PASS
Stanger Substation | Stanger-Gelnhills Feed (33KV) | Feeder | 101.77–105.04% | 0.9% | 1.0% | ok | 5 | PASS
Stanger Substation | Stanger-Groutville Phase1 (33KV) | Feeder | 99.78–108.16% | 1.6% | FAIL 3.71% | ok | 5 | FAIL FAIL
Stanger Substation | Stanger-Sappi Feed 1 (33KV) | Feeder | 101.8–105.17% | 0.9% | 0.97% | ok | 57 | PASS
Stanger Substation | Stanger-Sappi Feed 2 (33KV) | Feeder | 101.81–105.23% | 0.9% | 0.96% | ok | 6 | PASS

## Findings
Substation | Responsibility | Parameter | Where | Detail
Driefontein Substation's | ESKOM | unbalance | busbar (all feeders) | Busbar voltage unbalance breaches at the busbar — shared supply issue → Eskom point of supply
Shakaskraal Substation | ESKOM | unbalance | busbar (all feeders) | Busbar voltage unbalance breaches at the busbar — shared supply issue → Eskom point of supply
Stanger Substation | MUNICIPALITY | unbalance | 10266107 | Busbar voltage unbalance OK at busbar but failing on feeder(s) 10266107 → local network issue