## Summary
Meter | Read date | Checked | Pass | At limit (tighten) | Fail | Verdict | Failing parameters
Stanger-Feeder 1 (33KV) | 2026-06-23 11:29:21 SAST | 13 | 10 | 7 | 3 | REVIEW (3) | Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Stanger-Feeder 2 (33kV) | 2026-06-23 11:40:55 SAST | 13 | 9 | 7 | 4 | REVIEW (4) | Measurement Period 3 (PQ intervals); Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Stanger-Gelnhills Feed (33KV) | 2026-06-23 11:41:01 SAST | 13 | 10 | 7 | 3 | REVIEW (3) | Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Stanger-Groutville Phase1 (33KV) | 2026-06-23 11:40:56 SAST | 13 | 10 | 7 | 3 | REVIEW (3) | Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Stanger-Sappi Feed 1 (33KV) | 2026-06-27 12:46:37 SAST | 13 | 7 | 5 | 6 | REVIEW (6) | Measurement Period 3 (PQ intervals); Under Voltage sag 2 threshold; Power failure voltage cut threshold; Min. valid voltage (Umin ignore); Max. valid voltage (Umax ignore); Frequency limit
Stanger-Sappi Feed 2 (33KV) | 2026-06-23 11:41:06 SAST | 13 | 10 | 7 | 3 | REVIEW (3) | Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Shakaskraal-Feeder 1 (North) (33KV) | 2026-06-23 11:41:12 SAST | 13 | 9 | 7 | 4 | REVIEW (4) | Measurement Period 3 (PQ intervals); Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Shakaskraal-Feeder 2 (South) (33KV) | 2026-06-23 11:40:52 SAST | 13 | 9 | 7 | 4 | REVIEW (4) | Measurement Period 3 (PQ intervals); Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Ballito Sub (Feeder 1) (33KV) | 2026-06-23 11:41:05 SAST | 13 | 9 | 7 | 4 | REVIEW (4) | Measurement Period 3 (PQ intervals); Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
Zimbali Sub (Feeder 2) (33KV) | 2026-06-23 11:40:55 SAST | 13 | 9 | 7 | 4 | REVIEW (4) | Measurement Period 3 (PQ intervals); Under Voltage sag 2 threshold; Power failure voltage cut threshold; Frequency limit
— TOTAL — |  | 130 | 92 | 68 | 38 | 38 to review

## Threshold Comparison
Group | Parameter | Stanger-Feeder 1 (33KV) | Stanger-Feeder 2 (33kV) | Stanger-Gelnhills Feed (33KV) | Stanger-Groutville Phase1 (33KV) | Stanger-Sappi Feed 1 (33KV) | Stanger-Sappi Feed 2 (33KV) | Shakaskraal-Feeder 1 (North) (33KV) | Shakaskraal-Feeder 2 (South) (33KV) | Ballito Sub (Feeder 1) (33KV) | Zimbali Sub (Feeder 2) (33KV) | NRS 048-2 / EN 50160 | NRS Note
General / Nominal | nominal_voltage | — | — | — | — | — | — | — | — | — | — | 110 V | Secondary (VT measured)
General / Nominal | nominal_current | — | — | — | — | — | — | — | — | — | — | —
General / Nominal | Maximum current (Imax) | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | —
General / Nominal | nominal_frequency | — | — | — | — | — | — | — | — | — | — | 50 Hz | Nominal
General / Nominal | Measurement Period 3 (PQ intervals) | 600 s · 10 min | FAIL: 300 s · 5 min | 600 s · 10 min | 600 s · 10 min | FAIL: 60 s · 1 min | 600 s · 10 min | FAIL: 300 s · 5 min | FAIL: 300 s · 5 min | FAIL: 300 s · 5 min | FAIL: 300 s · 5 min | 600 s | NRS 048-2 — 10-min assessment window
CT / VT Ratios | ct_primary | — | — | — | — | — | — | — | — | — | — | — | CT primary current (site-specific)
CT / VT Ratios | ct_secondary | — | — | — | — | — | — | — | — | — | — | — | CT secondary — usually 1 A or 5 A
CT / VT Ratios | ct_ratio | — | — | — | — | — | — | — | — | — | — | — | CT ratio primary:secondary
CT / VT Ratios | vt_primary | — | — | — | — | — | — | — | — | — | — | — | VT primary voltage (line kV, site-specific)
CT / VT Ratios | vt_secondary | — | — | — | — | — | — | — | — | — | — | — | VT secondary — usually 110 V
CT / VT Ratios | vt_ratio | — | — | — | — | — | — | — | — | — | — | — | VT ratio primary:secondary
Over Voltage — Swell | Over Voltage swell threshold | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | 121 V (110% Vn) | ≥ 110% Vn (≥ 121 V) | EN 50160 §2 / NRS 048-2 — swell threshold
Over Voltage — Swell | Time threshold Over Voltage swell | 3 s | 1 s | 3 s | 3 s | 0 s | 0 s | 1 s | 1 s | 1 s | 1 s | 3 s typical | Meter config — time-to-event
Under Voltage — Sag 1 | Under Voltage sag 1 threshold | 99 V (90% Vn) | 99 V (90% Vn) | 99 V (90% Vn) | 99 V (90% Vn) | 104 V (94.5% Vn) | 99 V (90% Vn) | 99 V (90% Vn) | 99 V (90% Vn) | 99 V (90% Vn) | 99 V (90% Vn) | ≤ 90% Vn (≤ 99 V) | EN 50160 §2 / NRS 048-2 — sag definition
Under Voltage — Sag 1 | Time threshold Under Voltage sag 1 | 3 s | 1 s | 3 s | 3 s | 0 s | 0 s | 1 s | 1 s | 1 s | 1 s | 3 s typical | Meter dip-log persistence timer (≥10 ms defines a dip)
Under Voltage — Sag 2 | Under Voltage sag 2 threshold | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 83 V (75.5% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | FAIL: 4 V (3.6% Vn) | < 1% Vn (< 1.1 V) | Short interruption boundary
Under Voltage — Sag 2 | Time threshold Under Voltage sag 2 | 3 s | 1 s | 3 s | 3 s | 0 s | 0 s | 1 s | 1 s | 1 s | 1 s | ≤ 3 min · typ 3 s | Short vs long interruption boundary
Power Failure | Power failure voltage cut threshold | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (1.999 V) | FAIL: 1.8 % (2 V) | FAIL: 1.8 % (2 V) | < 1% Vn (< 1.1 V) | Power failure voltage cut threshold
Power Failure | Time threshold long power failure | 3 s | 1 s | 3 s | 3 s | 0 s | 0 s | 1 s | 1 s | 1 s | 1 s | > 3 min · typ 3 s | Long interruption — EN 50160 §5
Voltage Limits (W1) | Min. valid voltage (Umin ignore) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | FAIL: 8 % (→ 101.2 V) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | 15 % (→ 93.5 V) | 85% Vn (93.5 V) | Hard floor for valid data
Voltage Limits (W1) | Max. valid voltage (Umax ignore) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | FAIL: 8 % (→ 118.8 V) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | 15 % (→ 126.5 V) | 110% Vn (121 V) | Hard ceiling for valid data
Voltage Limits (W1) | Low voltage threshold Uunder | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | 10 % (→ 99 V) | ≥ 85% Vn (≥ 93.5 V) | Umin: 100% of week limit Vn − 15%
Voltage Limits (W1) | High voltage threshold Uover | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | 10 % (→ 121 V) | ≤ 110% Vn (≤ 121 V) | Umax: 100% of week limit Vn + 10%
Voltage Limits (W1) | Threshold slow voltage changes (W1) | 95.0 % | 95.0 % | 95.0 % | 95.0 % | 95.0 % | 95.0 % | 95.0 % | 95.0 % | 95.0 % | 95.0 % | —
THD Limits (W2) | Voltage THD limit (W2) | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | ≤ 8% | EN 50160 §4 / NRS 048-2 — THD_u 95% of week
THD Limits (W2) | Current THD limit (W2) | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | 8.0 % | ≤ 8% | Current THD reference limit
Unbalance (W3) | Voltage unbalance limit (W3) | 2.0 % | 2.0 % | 2.0 % | 2.0 % | 2.0 % | 2.0 % | 2.0 % | 2.0 % | 2.0 % | 2.0 % | ≤ 2% | NRS 048-2 §3 LV/MV — neg seq / pos seq ratio
Frequency | Frequency limit | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | FAIL: 2 % (± 1 Hz) | ±1% (± 0.5 Hz) | EN 50160 §1 — 99.5% of year
Neutral Wire | Missing neutral wire deviation | [8, 12] | [8, 12] | [8, 12] | [8, 12] | [8, 12] | [8, 12] | [8, 12] | [8, 12] | [8, 12] | [8, 12] | —

## NRS 048-2 Reference
Parameter | Limit | Target / Window | Source
Voltage magnitude | Vn ± 10% | ≥ 95% of week (10-min avg) | EN 50160 §2 / NRS 048-2
Voltage magnitude (abs) | Vn +10% / −15% | 100% of week | EN 50160 §2 / NRS 048-2
THD_u (voltage) | ≤ 8% | ≥ 95% of week (10-min avg) | EN 50160 §4 / NRS 048-2
Voltage unbalance (LV/MV) | ≤ 2% | ≥ 95% of week (10-min avg) | NRS 048-2 §3
Frequency (interconnected) | ± 1% (49.5–50.5 Hz) | ≥ 99.5% of year (10-s interval) | EN 50160 §1 / NRS 048-2
Frequency (abs limit) | 47–52 Hz | 100% of time | EN 50160 §1
Flicker Plt | ≤ 1.0 | ≥ 95% of week (2-hr Plt window) | EN 50160 §3
Voltage sag (dip) | < 90% Vn | Log all events | EN 50160 §2
Voltage swell | > 110% Vn | Log all events | EN 50160 §2
Short interruption | < 1% Vn for < 3 min | Log all events | EN 50160 §5
Long interruption | < 1% Vn for ≥ 3 min | Log all events + duration | EN 50160 §5
Harmonic H3 | ≤ 5.0% Vn | ≥ 95% of week | EN 50160 Table 1
Harmonic H5 | ≤ 6.0% Vn | ≥ 95% of week | EN 50160 Table 1
Harmonic H7 | ≤ 5.0% Vn | ≥ 95% of week | EN 50160 Table 1
Harmonic H11 | ≤ 3.5% Vn | ≥ 95% of week | EN 50160 Table 1
Harmonic H13 | ≤ 3.0% Vn | ≥ 95% of week | EN 50160 Table 1
Data availability | ≥ 95% of intervals | Per meter per month | NRS 048-2 / NERSA